## Sheet2
| CALCULATE THE SIZE OF BATTERY BANK & INVERTOR | [9 empty] | Jignesh.Parmar www.electricalnotes.wordpress.com jiguparmar@yahoo.com
Electrical Load Details | [7 empty] | Battery Bank's Voltage | 12 | Volts DC
Sr.No | Equiment Name | No | Watt | Using Hr/Day | Watt Hr./Day |  |  | Reaserve Day: (How many days Do you want to get Power from battery Banks) | 2.5 | Days
1 |  | 1 | 100 | 1 | 100 | 100
[5 empty] | 0 | 0 |  | Loose Connection/Wire Loss Factor: | 20 | % | 0.2
[5 empty] | 0 | 0 |  | Battery Efficiency | 100 | % | 1
[5 empty] | 0 | 0 |  | Battery Aging: | 20 | % | 0.2
[5 empty] | 0 | 0 |  | Depth of Discharge:(DOD) | 50 | % | 0.5
[5 empty] | 0 | 0 |  | Battery Operating Temp: | 46
[5 empty] | 0 | 0 |  | The Battery Bank Required: | 60 | Amp.Hr
[5 empty] | 0 | 0 | [6 empty] | 1
[5 empty] | 0 | 0 |  | If You are Selecting Battery | 50 | Amp.Hr @ | 6 | volts | 2 | 0
[5 empty] | 0 | 0 |  | Batteries connection for Battery Bank
[5 empty] | 0 | 0
[5 empty] | 0 | 0 |  | :Battery Bank Detail :
[5 empty] | 0 | 0 |  | Type of Connection For Batteries | Series-Parral Connection
[5 empty] | 0 | 0 |  | Selection of Batteries Connection: | O.K
[5 empty] | 0 | 0 |  | Selection of Each Battery Voltage | O.K
[5 empty] | 0 | 0 |  | Number of String for Battry Bank | 1 | Nos
[5 empty] | 0 | 0 |  | Total Amp.Hr of Each String | 50 | Amp.Hr | [12 empty] | C | F
[5 empty] | 0 | 0 |  | Total No of Battery in Each String | 2 | Nos | [12 empty] | 6.7 | 20 | 1.59
[5 empty] | 0 | 0 | [16 empty] | 1.1 | 30 | 1.4
[5 empty] | 0 | 0 |  | Total Battery Bank Amp.Hr | 50 | Amp.Hr | [12 empty] | 4 | 40 | 1.3
[5 empty] | 0 | 0 |  | Total Nos of Batteries in Battery Bank | 2 | Nos | [12 empty] | 10 | 50 | 1.19
[5 empty] | 0 | 0 | [16 empty] | 15.6 | 60 | 1.11
[5 empty] | 0 | 0 | :Size of Invertor: | [15 empty] | 21.2 | 70 | 1.04
[5 empty] | 0 | 0 |  | Calculate Additional Future Load | 20 | % | [12 empty] | 26.7 | 80 | 1
[5 empty] | 0 | 0 |  | Effieciency of Invertor | 80 | %
[5 empty] | 0 | 0 |  | Size of Invertor | 150 | KW
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0 |  | CALCULATIONS: | [10 empty] | string | amp.hr | No | Total
[5 empty] | 0 | 0 |  | Total KW.Hr/Day | 100 | Watt.Hr/Day |  |  |  |  | 0 |  | series | 50 | 1 | 1 | 2 | 2 | C° | 1
[5 empty] | 0 | 0 |  | Total Amp.Hr | 8.3333 | Amp.Hr |  |  |  |  | 0 |  | Parral | 50 | 1 | 1 | 2 | 2 | F° | 1.3
[5 empty] | 0 | 0 |  | Average Load | 10 | Amp.Hr |  |  |  |  | 1 |  | series-Parral | 50 | 1 | 1 | 2 | 2 | 1 | 1
[5 empty] | 0 | 0 |  | Storage Required | 25 | Amp.Hr | [12 empty] | Series | 3
[5 empty] | 0 | 0 |  | Battery Aging | 30 | Amp.Hr | [12 empty] | Parral
[5 empty] | 0 | 0 |  | Including Operating Temp | 30 | Amp.Hr | [5 empty] | 1 | Select other Type of Connecion | [5 empty] | Series-Parral
[5 empty] | 0 | 0 |  | Depth of Discharge | 60 | Amp.Hr | [5 empty] | 2 | Select other Type of Connecion
[5 empty] | 0 | 0 | [9 empty] | 3 | O.K | 50 | 1 | 1 | 2 | 2
[5 empty] | 0 | 0
Total Load |  |  |  |  | 100 | 100 | Watt.Hr/Day