## Calculations
Calculations Based On Motor HP
Input Data |  | Calculated Values
Motor Voltage (V L-L) |  | Operating Current (A) | 7.6
Motor HP |  | 125% Current per NEC (A) | 9.5
Cable Temperature Rating (°C) |  | "Zero Length" Cable Size | 14 | AWG | Conductor Table position based on "zero length" ampacity: |  |  |  | 24
Ambient Temperature (°C) |  | Acceptable Voltage Drop (V) | 7.9674
Cable Length (ft) | 500 | Recommended Cable Size | 12 | AWG | Conductor Table position based on voltage drop: |  |  |  | 23
Acceptable Voltage Drop (%) | 3% | Actual Voltage Drop (V) | 6.46
|  | Actual Voltage Drop (%) | 2.432%
Calculations Based On Specified Current
Input Data |  | Calculated Values
Operating Voltage (V L-L) | 460 | "Zero Length" Cable Size | 14 | AWG | Conductor Table position based on "zero length" ampacity: |  |  |  | 24
Specified Current (A) | 7.6 | Acceptable Voltage Drop (V) | 7.9674
Cable Temperature Rating (°C) |  | Recommended Cable Size | 12 | AWG | Conductor Table position based on voltage drop: |  |  |  | 23
Ambient Temperature (°C) |  | Actual Voltage Drop (V) | 6.46
Cable Length (ft) | 500 | Actual Voltage Drop (%) | 2.432%
Acceptable Voltage Drop (%) | 3%
[6 empty] | 208 | 0.5 |  | 75 | 75
Note: Data entry is only possible in areas highlighted in yellow. | [5 empty] | 230 | 0.75 |  | 90 | 90
[6 empty] | 460 | 1
Conductor ampacities are based on NEC 2008, Table 310.16 (Not more than 3 current carrying conductors in racewary). | [5 empty] | 575 | 1.5 |  | 1 | 1
Conductor impedances are based on NEC 2008, Chapter 9, Table 9. | [6 empty] | 2 | Temperature | 75 | 75
[6 empty] | 3 | 3
[5 empty] | Voltage | 460 | 5 |  | 21-25 | 21-25
[7 empty] | 7.5 |  | 26-30 (std) | 26-30 (std)
[7 empty] | 10 |  | 31-35 | 31-35
[7 empty] | 15 |  | 36-40 | 36-40
[7 empty] | 20 |  | 41-45 | 41-45
[7 empty] | 25 |  | 46-50 | 46-50
[7 empty] | 30 |  | 51-55 | 51-55
40
[7 empty] | 50 | De-rate factor position | 2 | 2
60
75
100
125
150
200
250
300
350
400
450
500
7
[6 empty] | HP | 5

## Motor Table
Rated Currents Vs. HP and Voltage
Voltage
HP | 208 | 230 | 460 | 575
0.5 | 2.4 | 2.2 | 1.1 | 0.9
0.75 | 3.5 | 3.2 | 1.6 | 1.3
1 | 4.6 | 4.2 | 2.1 | 1.7
1.5 | 6.6 | 6 | 3 | 2.4
2 | 7.5 | 6.8 | 3.4 | 2.7
3 | 10.6 | 9.6 | 4.8 | 3.9
5 | 16.7 | 15.2 | 7.6 | 6.1
7.5 | 24.2 | 22 | 11 | 9
10 | 30.8 | 28 | 14 | 11
15 | 46.2 | 42 | 21 | 17
20 | 59.4 | 54 | 27 | 22
25 | 74.8 | 68 | 34 | 27
30 | 88 | 80 | 40 | 32
40 | 114 | 104 | 52 | 41
50 | 143 | 130 | 65 | 52
60 | 169 | 154 | 77 | 62
75 | 211 | 192 | 96 | 77
100 | 273 | 248 | 124 | 99
125 | 343 | 312 | 156 | 125
150 | 396 | 360 | 180 | 144
200 | 528 | 480 | 240 | 192
250 | #N/A | #N/A | 302 | 242
300 | #N/A | #N/A | 361 | 289
350 | #N/A | #N/A | 414 | 336
400 | #N/A | #N/A | 477 | 382
450 | #N/A | #N/A | 515 | 412
500 | #N/A | #N/A | 590 | 472

## Conductor Tables
Cable Ampacity (Table 310-16)
AWG or kcmil | 75 | Motor HP with 75 De-rate | Specified Current with 75 De-rate | 90 | Motor HP with 90 De-rate | Specified Current with 90 De-rate | AWG or kcmil | 60Hz Impedance per 1000 ft | Voltage Drop Based On Motor HP | Voltage Drop Based On Operating Current | Label
4 x 350 | 1240 | 1240 | 1240 | 1400 | 1400 | 1400 | 4 x 350 | 0.015 | 0.057 | 0.057 | kcmil
3 x 500 | 1140 | 1140 | 1140 | 1290 | 1290 | 1290 | 3 x 500 | 0.016667 | 0.063333 | 0.063333 | kcmil
4 x 250 | 1020 | 1020 | 1020 | 1160 | 1160 | 1160 | 4 x 250 | 0.01825 | 0.06935 | 0.06935 | kcmil
3 x 350 | 930 | 930 | 930 | 1050 | 1050 | 1050 | 3 x 350 | 0.02 | 0.076 | 0.076 | kcmil
2 x 500 | 760 | 760 | 760 | 860 | 860 | 860 | 2 x 500 | 0.025 | 0.095 | 0.095 | kcmil
3 x 4/0 | 690 | 690 | 690 | 780 | 780 | 780 | 3 x 4/0 | 0.026667 | 0.10133 | 0.10133 | AWG
2 x 350 | 620 | 620 | 620 | 700 | 700 | 700 | 2 x 350 | 0.03 | 0.114 | 0.114 | kcmil
2 x 250 | 510 | 510 | 510 | 580 | 580 | 580 | 2 x 250 | 0.0365 | 0.1387 | 0.1387 | kcmil
2 x 4/0 | 460 | 460 | 460 | 520 | 520 | 520 | 2 x 4/0 | 0.04 | 0.152 | 0.152 | AWG
500 | 380 | 380 | 380 | 430 | 430 | 430 | 500 | 0.05 | 0.19 | 0.19 | kcmil
350 | 310 | 310 | 310 | 350 | 350 | 350 | 350 | 0.06 | 0.228 | 0.228 | kcmil
250 | 255 | 255 | 255 | 290 | 290 | 290 | 250 | 0.073 | 0.2774 | 0.2774 | kcmil
4/0 | 230 | 230 | 230 | 260 | 260 | 260 | 4/0 | 0.08 | 0.304 | 0.304 | AWG
3/0 | 200 | 200 | 200 | 225 | 225 | 225 | 3/0 | 0.094 | 0.3572 | 0.3572 | AWG
2/0 | 175 | 175 | 175 | 195 | 195 | 195 | 2/0 | 0.11 | 0.418 | 0.418 | AWG
1/0 | 150 | 150 | 150 | 170 | 170 | 170 | 1/0 | 0.13 | 0.494 | 0.494 | AWG
1 | 130 | 130 | 130 | 150 | 150 | 150 | 1 | 0.16 | 0.608 | 0.608 | AWG
2 | 115 | 115 | 115 | 130 | 130 | 130 | 2 | 0.2 | 0.76 | 0.76 | AWG
4 | 85 | 85 | 85 | 95 | 95 | 95 | 4 | 0.3 | 1.14 | 1.14 | AWG
6 | 65 | 65 | 65 | 75 | 75 | 75 | 6 | 0.45 | 1.71 | 1.71 | AWG
8 | 50 | 50 | 50 | 55 | 55 | 55 | 8 | 0.7 | 2.66 | 2.66 | AWG
10 | 35 | 35 | 35 | 40 | 40 | 40 | 10 | 1.1 | 4.18 | 4.18 | AWG
12 | 25 | 25 | 25 | 30 | 30 | 30 | 12 | 1.7 | 6.46 | 6.46 | AWG
14 | 20 | 20 | 20 | 25 | 25 | 25 | 14 | 2.7 | 10.26 | 10.26 | AWG
Applied De-rate factor |  | 1 | 1 |  | 1 | 1
De-rate factors | 75 | 90
21-25 | 1.05 | 1.04
26-30 (std) | 1 | 1
31-35 | 0.94 | 0.96
36-40 | 0.88 | 0.91
41-45 | 0.82 | 0.87
46-50 | 0.75 | 0.82
51-55 | 0.67 | 0.76