## CPU
FOR CPU PANEL
Description | TYPE | Power Diss(W). per module | QTY | Total Power Dissipated(W)
PS407, POWER SUPPLY UNIT, 24VDC/10A | 6ES7 407-0KA02-0AA0 | 105 | 4 | 420
CPU 417-4 2H | 6ES7 417-4HT14-0AB0 | 6.5 | 4 | 26
COMMUNICATION PROCESSOR, CP443-1 | 6ES7 1EX20-0XE0 | 8.6 | 4 | 34.4
ETHERNET SWITCH, 16PORTS, MANAGED TYPE, RJ45 | MCS 16TX | 14.4 | 2 | 28.8
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/6A | 6EP1233-1AA00 | 150 | 2 | 300
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/12A | 6EP1234-1AA00 | 300 | 0 | 0
REDUNDANCY DIODE MODULE, 24VDC/10A | ULPEDDIO-10A | 8 | 1 | 8
REDUNDANCY DIODE MODULE, 24VDC/20A | ULPEDDIO-20A | 10 | 0 | 0
COOLING FAN WITH FILTER ASSEMBLY, 230VAC, RAL7035 | SK3323.107 | 19 | 2 | 38
PANEL TUBE LIGHT, 230VAC/11W | FMS200/111 | 11 | 1 | 11
LED INDICATION LAMP, 230VAC, RED (FOR 230VAC SUPPLY ON INDICATION) | 3SB14 01-2WZ3 | 1.5 | 3 | 4.5
LED INDICATION LAMP, 24VDC, GREEN (FOR 24VDC POWER SUPPLY ON INDICATION) | 3SB14 02-2HZ | 1.5 | 2 | 3
20% EXTRA | --- | 174.74 | 0 | 0
TOTAL (Watt) |  |  |  | 873.7
Flow Rates are often given as ‘cubic feet per minute’ (cfm), so to convert to cubic meters per minute (m3/min) use the following multiplier:
m3/min = cfm x 0.0283
Air Flow for Rittal (SK3323.107) Fan (m3/hr) | 105
Total Fan used in panel are: | 2
So Air flow in Cubical is = (Air flow x fan qty) x 0.0283 | 5.943
= m3/min | 5.943
FORMULA
TEMP RISE IN PANEL | TOTAL POWER DISSIPATED (W) x 0.053
AIR FLOW IN CUBICAL(m3/min)
TEMP RISE IN PANEL | 7.7917
TOTAL TEMP RISE | = AMBIENT MAX.TEMP + TEMP RISE IN PANEL
| 37.7917 | Deg C

## CABINET-1
FOR MARSHALING CABINET-1
Description | TYPE | Power Diss(W). per module | QTY | Total Power Dissipated(W)
IM153-2, INTERFACE MODULE | 6ES7 153-2BA02-0XB0 | 5.5 | 10 | 55
CP341 WITH RS422 / RS485 INTERFACE | 6ES7 341-1CH02-0AE0 | 2.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, 4-20mA | 6ES7 331-1KF01-0AB0 | 0.4 | 55 | 22
SM 331, 8 CHANNEL ANALOG I/P CARD T/C, 4-20mA | 6ES7 331-7KF02-0AB0 | 1 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, RTD | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG O/P CARD, 4-20mA | 6ES7 332-5HF00-0AB0 | 6 | 0 | 0
SM 321, 32 CHANNEL DIGITAL I/P CARD | 6ES7 321-1BL00-0AA0 | 6.5 | 0 | 0
SM 321, 16 CHANNEL SOE DIGITAL I/P CARD, 24VDC | 6ES7 321-7BH01-0AB0 | 4 | 0 | 0
SM 322, 32 CHANNEL DIGITAL O/P CARD | 6ES7 322-1BL00-0AA0 | 6.6 | 0 | 0
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/6A | 6EP1233-1AA00 | 150 | 2 | 300
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/12A | 6EP1234-1AA00 | 300 | 4 | 1200
REDUNDANCY DIODE MODULE, 24VDC/10A | ULPEDDIO-10A | 8 | 1 | 8
REDUNDANCY DIODE MODULE, 24VDC/20A | ULPEDDIO-20A | 10 | 2 | 20
COOLING FAN WITH FILTER ASSEMBLY, 230VAC, RAL7035 | SK3323.107 | 19 | 4 | 76
PANEL TUBE LIGHT, 230VAC/11W | FMS200/111 | 11 | 4 | 44
LED INDICATION LAMP, 230VAC, RED (FOR 230VAC SUPPLY ON INDICATION) | 3SB14 01-2WZ3 | 1.5 | 3 | 4.5
LED INDICATION LAMP, 24VDC, GREEN (FOR 24VDC POWER SUPPLY ON INDICATION) | 3SB14 02-2HZ | 1.5 | 6 | 9
20% EXTRA | --- | 347.7 | 1 | 347.7
TOTAL (Watt) |  |  |  | 2086.2
Flow Rates are often given as ‘cubic feet per minute’ (cfm), so to convert to cubic meters per minute (m3/min) use the following multiplier:
m3/min = cfm x 0.0283
Air Flow for Rittal (SK3323.107) Fan (m3/hr) | 105
Total Fan used in panel are: | 4
So Air flow in Cubical is = (Air flow x fan qty) x 0.0283 | 11.886
= m3/min | 11.886
FORMULA
TEMP RISE IN PANEL | TOTAL POWER DISSIPATED (W) x 0.053
AIR FLOW IN CUBICAL(m3/min)
TEMP RISE IN PANEL | 9.3024
TOTAL TEMP RISE | = AMBIENT MAX.TEMP(30degC) + TEMP RISE IN PANEL
| 39.3024 | Deg C

## CABINET-2
FOR MARSHALING CABINET-2
Description | TYPE | Power Diss(W). per module | QTY | Total Power Dissipated(W)
IM153-2, INTERFACE MODULE | 6ES7 153-2BA02-0XB0 | 5.5 | 10 | 55
CP341 WITH RS422 / RS485 INTERFACE | 6ES7 341-1CH02-0AE0 | 2.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, 4-20mA | 6ES7 331-1KF01-0AB0 | 0.4 | 1 | 0.4
SM 331, 8 CHANNEL ANALOG I/P CARD T/C, 4-20mA | 6ES7 331-7KF02-0AB0 | 1 | 11 | 11
SM 331, 8 CHANNEL ANALOG I/P CARD, RTD | 6ES7 331-1KF01-0AB0 | 0.4 | 25 | 10
SM 331, 8 CHANNEL ANALOG O/P CARD, 4-20mA | 6ES7 332-5HF00-0AB0 | 6 | 14 | 84
SM 321, 32 CHANNEL DIGITAL I/P CARD | 6ES7 321-1BL00-0AA0 | 6.5 | 4 | 26
SM 321, 16 CHANNEL SOE DIGITAL I/P CARD, 24VDC | 6ES7 321-7BH01-0AB0 | 4 | 0 | 0
SM 322, 32 CHANNEL DIGITAL O/P CARD | 6ES7 322-1BL00-0AA0 | 6.6 | 0 | 0
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/6A | 6EP1233-1AA00 | 150 | 2 | 300
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/12A | 6EP1234-1AA00 | 300 | 6 | 1800
REDUNDANCY DIODE MODULE, 24VDC/10A | ULPEDDIO-10A | 8 | 1 | 8
REDUNDANCY DIODE MODULE, 24VDC/20A | ULPEDDIO-20A | 10 | 3 | 30
COOLING FAN WITH FILTER ASSEMBLY, 230VAC, RAL7035 | SK3323.107 | 19 | 4 | 76
PANEL TUBE LIGHT, 230VAC/11W | FMS200/111 | 11 | 4 | 44
LED INDICATION LAMP, 230VAC, RED (FOR 230VAC SUPPLY ON INDICATION) | 3SB14 01-2WZ3 | 1.5 | 3 | 4.5
LED INDICATION LAMP, 24VDC, GREEN (FOR 24VDC POWER SUPPLY ON INDICATION) | 3SB14 02-2HZ | 1.5 | 8 | 12
20% EXTRA | --- | 492.18 | 1 | 492.18
TOTAL (Watt) |  |  |  | 2953.08
Flow Rates are often given as ‘cubic feet per minute’ (cfm), so to convert to cubic meters per minute (m3/min) use the following multiplier:
m3/min = cfm x 0.0283
Air Flow for Rittal (SK3323.107) Fan (m3/hr) | 105
Total Fan used in panel are: | 4
So Air flow in Cubical is = (Air flow x fan qty) x 0.0283 | 11.886
= m3/min | 11.886
FORMULA
TEMP RISE IN PANEL | TOTAL POWER DISSIPATED (W) x 0.053
AIR FLOW IN CUBICAL(m3/min)
TEMP RISE IN PANEL | 13.1679
TOTAL TEMP RISE | = AMBIENT MAX.TEMP + TEMP RISE IN PANEL
| 43.1679 | Deg C

## CABINET-3
FOR MARSHALING CABINET-3
Description | TYPE | Power Diss(W). per module | QTY | Total Power Dissipated(W)
IM153-2, INTERFACE MODULE | 6ES7 153-2BA02-0XB0 | 5.5 | 4 | 22
CP341 WITH RS422 / RS485 INTERFACE | 6ES7 341-1CH02-0AE0 | 2.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, 4-20mA | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD T/C, 4-20mA | 6ES7 331-7KF02-0AB0 | 1 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, RTD | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG O/P CARD, 4-20mA | 6ES7 332-5HF00-0AB0 | 6 | 0 | 0
SM 321, 32 CHANNEL DIGITAL I/P CARD | 6ES7 321-1BL00-0AA0 | 6.5 | 22 | 143
SM 321, 16 CHANNEL SOE DIGITAL I/P CARD, 24VDC | 6ES7 321-7BH01-0AB0 | 4 | 0 | 0
SM 322, 32 CHANNEL DIGITAL O/P CARD | 6ES7 322-1BL00-0AA0 | 6.6 | 0 | 0
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/6A | 6EP1233-1AA00 | 150 | 2 | 300
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/12A | 6EP1234-1AA00 | 300 | 8 | 2400
REDUNDANCY DIODE MODULE, 24VDC/10A | ULPEDDIO-10A | 8 | 1 | 8
REDUNDANCY DIODE MODULE, 24VDC/20A | ULPEDDIO-20A | 10 | 4 | 40
COOLING FAN WITH FILTER ASSEMBLY, 230VAC, RAL7035 | SK3323.107 | 19 | 3 | 57
PANEL TUBE LIGHT, 230VAC/11W | FMS200/111 | 11 | 6 | 66
LED INDICATION LAMP, 230VAC, RED (FOR 230VAC SUPPLY ON INDICATION) | 3SB14 01-2WZ3 | 1.5 | 3 | 4.5
LED INDICATION LAMP, 24VDC, GREEN (FOR 24VDC POWER SUPPLY ON INDICATION) | 3SB14 02-2HZ | 1.5 | 10 | 15
20% EXTRA | --- | 611.1 | 1 | 611.1
TOTAL (Watt) |  |  |  | 3666.6
Flow Rates are often given as ‘cubic feet per minute’ (cfm), so to convert to cubic meters per minute (m3/min) use the following multiplier:
m3/min = cfm x 0.0283
Air Flow for Rittal (SK3323.107) Fan (m3/hr) | 105
Total Fan used in panel are: | 3
So Air flow in Cubical is = (Air flow x fan qty) x 0.0283 | 89.145
= m3/min | 89.145
FORMULA
TEMP RISE IN PANEL | TOTAL POWER DISSIPATED (W) x 0.053
AIR FLOW IN CUBICAL(m3/min)
TEMP RISE IN PANEL | 2.1799
TOTAL TEMP RISE | = AMBIENT MAX.TEMP + TEMP RISE IN PANEL
| 32.1799 | Deg C

## CABINET-4
FOR MARSHALING CABINET-4
Description | TYPE | Power Diss(W). per module | QTY | Total Power Dissipated(W)
IM153-2, INTERFACE MODULE | 6ES7 153-2BA02-0XB0 | 5.5 | 4 | 22
CP341 WITH RS422 / RS485 INTERFACE | 6ES7 341-1CH02-0AE0 | 2.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, 4-20mA | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD T/C, 4-20mA | 6ES7 331-7KF02-0AB0 | 1 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, RTD | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG O/P CARD, 4-20mA | 6ES7 332-5HF00-0AB0 | 6 | 0 | 0
SM 321, 32 CHANNEL DIGITAL I/P CARD | 6ES7 321-1BL00-0AA0 | 6.5 | 22 | 143
SM 321, 16 CHANNEL SOE DIGITAL I/P CARD, 24VDC | 6ES7 321-7BH01-0AB0 | 4 | 0 | 0
SM 322, 32 CHANNEL DIGITAL O/P CARD | 6ES7 322-1BL00-0AA0 | 6.6 | 0 | 0
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/6A | 6EP1233-1AA00 | 150 | 2 | 300
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/12A | 6EP1234-1AA00 | 300 | 8 | 2400
REDUNDANCY DIODE MODULE, 24VDC/10A | ULPEDDIO-10A | 8 | 1 | 8
REDUNDANCY DIODE MODULE, 24VDC/20A | ULPEDDIO-20A | 10 | 4 | 40
COOLING FAN WITH FILTER ASSEMBLY, 230VAC, RAL7035 | SK3323.107 | 19 | 3 | 57
PANEL TUBE LIGHT, 230VAC/11W | FMS200/111 | 11 | 6 | 66
LED INDICATION LAMP, 230VAC, RED (FOR 230VAC SUPPLY ON INDICATION) | 3SB14 01-2WZ3 | 1.5 | 3 | 4.5
LED INDICATION LAMP, 24VDC, GREEN (FOR 24VDC POWER SUPPLY ON INDICATION) | 3SB14 02-2HZ | 1.5 | 10 | 15
20% EXTRA | --- | 611.1 | 1 | 611.1
TOTAL (Watt) |  |  |  | 3666.6
Flow Rates are often given as ‘cubic feet per minute’ (cfm), so to convert to cubic meters per minute (m3/min) use the following multiplier:
m3/min = cfm x 0.0283
Air Flow for Rittal (SK3323.107) Fan (m3/hr) | 105
Total Fan used in panel are: | 3
So Air flow in Cubical is = (Air flow x fan qty) x 0.0283 | 89.145
= m3/min | 89.145
FORMULA
TEMP RISE IN PANEL = | TOTAL POWER DISSIPATED (W) x 0.053
AIR FLOW IN CUBICAL(m3/min)
TEMP RISE IN PANEL = | 2.1799
TOTAL TEMP RISE | = AMBIENT MAX.TEMP + TEMP RISE IN PANEL
| 32.1799 | Deg C

## CABINET-5
FOR MARSHALING CABINET-5
Description | TYPE | Power Diss(W). per module | QTY | Total Power Dissipated(W)
IM153-2, INTERFACE MODULE | 6ES7 153-2BA02-0XB0 | 5.5 | 4 | 22
CP341 WITH RS422 / RS485 INTERFACE | 6ES7 341-1CH02-0AE0 | 2.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, 4-20mA | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD T/C, 4-20mA | 6ES7 331-7KF02-0AB0 | 1 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, RTD | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG O/P CARD, 4-20mA | 6ES7 332-5HF00-0AB0 | 6 | 0 | 0
SM 321, 32 CHANNEL DIGITAL I/P CARD | 6ES7 321-1BL00-0AA0 | 6.5 | 11 | 71.5
SM 321, 16 CHANNEL SOE DIGITAL I/P CARD, 24VDC | 6ES7 321-7BH01-0AB0 | 4 | 0 | 0
SM 322, 32 CHANNEL DIGITAL O/P CARD | 6ES7 322-1BL00-0AA0 | 6.6 | 11 | 72.6
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/6A | 6EP1233-1AA00 | 150 | 2 | 300
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/12A | 6EP1234-1AA00 | 300 | 6 | 1800
REDUNDANCY DIODE MODULE, 24VDC/10A | ULPEDDIO-10A | 8 | 1 | 8
REDUNDANCY DIODE MODULE, 24VDC/20A | ULPEDDIO-20A | 10 | 3 | 30
COOLING FAN WITH FILTER ASSEMBLY, 230VAC, RAL7035 | SK3323.107 | 19 | 3 | 57
PANEL TUBE LIGHT, 230VAC/11W | FMS200/111 | 11 | 6 | 66
LED INDICATION LAMP, 230VAC, RED (FOR 230VAC SUPPLY ON INDICATION) | 3SB14 01-2WZ3 | 1.5 | 3 | 4.5
LED INDICATION LAMP, 24VDC, GREEN (FOR 24VDC POWER SUPPLY ON INDICATION) | 3SB14 02-2HZ | 1.5 | 8 | 12
20% EXTRA | --- | 488.72 | 1 | 488.72
TOTAL (Watt) |  |  |  | 2932.32
Flow Rates are often given as ‘cubic feet per minute’ (cfm), so to convert to cubic meters per minute (m3/min) use the following multiplier:
m3/min = cfm x 0.0283
Air Flow for Rittal (SK3323.107) Fan (m3/hr) | 105
Total Fan used in panel are: | 3
So Air flow in Cubical is = (Air flow x fan qty) x 0.0283 | 89.145
= m3/min | 89.145
FORMULA
TEMP RISE IN PANEL | TOTAL POWER DISSIPATED (W) x 0.053
AIR FLOW IN CUBICAL(m3/min)
TEMP RISE IN PANEL | 1.7434
TOTAL TEMP RISE | = AMBIENT MAX.TEMP + TEMP RISE IN PANEL
| 31.7434 | Deg C

## CABINET-6
FOR MARSHALING CABINET-6
Description | TYPE | Power Diss(W). per module | QTY | Total Power Dissipated(W)
IM153-2, INTERFACE MODULE | 6ES7 153-2BA02-0XB0 | 5.5 | 4 | 22
CP341 WITH RS422 / RS485 INTERFACE | 6ES7 341-1CH02-0AE0 | 2.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, 4-20mA | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD T/C, 4-20mA | 6ES7 331-7KF02-0AB0 | 1 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, RTD | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG O/P CARD, 4-20mA | 6ES7 332-5HF00-0AB0 | 6 | 0 | 0
SM 321, 32 CHANNEL DIGITAL I/P CARD | 6ES7 321-1BL00-0AA0 | 6.5 | 0 | 0
SM 321, 16 CHANNEL SOE DIGITAL I/P CARD, 24VDC | 6ES7 321-7BH01-0AB0 | 4 | 0 | 0
SM 322, 32 CHANNEL DIGITAL O/P CARD | 6ES7 322-1BL00-0AA0 | 6.6 | 21 | 138.6
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/6A | 6EP1233-1AA00 | 150 | 2 | 300
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/12A | 6EP1234-1AA00 | 300 | 4 | 1200
REDUNDANCY DIODE MODULE, 24VDC/10A | ULPEDDIO-10A | 8 | 1 | 8
REDUNDANCY DIODE MODULE, 24VDC/20A | ULPEDDIO-20A | 10 | 2 | 20
COOLING FAN WITH FILTER ASSEMBLY, 230VAC, RAL7035 | SK3323.107 | 19 | 3 | 57
PANEL TUBE LIGHT, 230VAC/11W | FMS200/111 | 11 | 6 | 66
LED INDICATION LAMP, 230VAC, RED (FOR 230VAC SUPPLY ON INDICATION) | 3SB14 01-2WZ3 | 1.5 | 3 | 4.5
LED INDICATION LAMP, 24VDC, GREEN (FOR 24VDC POWER SUPPLY ON INDICATION) | 3SB14 02-2HZ | 1.5 | 6 | 9
20% EXTRA | --- | 365.02 | 1 | 365.02
TOTAL (Watt) |  |  |  | 2190.12
Flow Rates are often given as ‘cubic feet per minute’ (cfm), so to convert to cubic meters per minute (m3/min) use the following multiplier:
m3/min = cfm x 0.0283
Air Flow for Rittal (SK3323.107) Fan (m3/hr) | 105
Total Fan used in panel are: | 3
So Air flow in Cubical is = (Air flow x fan qty) x 0.0283 | 89.145
= m3/min | 89.145
FORMULA
TEMP RISE IN PANEL | TOTAL POWER DISSIPATED (W) x 0.053
AIR FLOW IN CUBICAL(m3/min)
TEMP RISE IN PANEL | 1.3021
TOTAL TEMP RISE | = AMBIENT MAX.TEMP + TEMP RISE IN PANEL
| 31.3021 | Deg C

## CABINET-7
FOR MARSHALING CABINET-7
Description | TYPE | Power Diss(W). per module | QTY | Total Power Dissipated(W)
IM153-2, INTERFACE MODULE | 6ES7 153-2BA02-0XB0 | 5.5 | 8 | 44
CP341 WITH RS422 / RS485 INTERFACE | 6ES7 341-1CH02-0AE0 | 2.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, 4-20mA | 6ES7 331-1KF01-0AB0 | 0.4 | 29 | 11.6
SM 331, 8 CHANNEL ANALOG I/P CARD T/C, 4-20mA | 6ES7 331-7KF02-0AB0 | 1 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, RTD | 6ES7 331-1KF01-0AB0 | 0.4 | 5 | 2
SM 331, 8 CHANNEL ANALOG O/P CARD, 4-20mA | 6ES7 332-5HF00-0AB0 | 6 | 4 | 24
SM 321, 32 CHANNEL DIGITAL I/P CARD | 6ES7 321-1BL00-0AA0 | 6.5 | 0 | 0
SM 321, 16 CHANNEL SOE DIGITAL I/P CARD, 24VDC | 6ES7 321-7BH01-0AB0 | 4 | 4 | 16
SM 322, 32 CHANNEL DIGITAL O/P CARD | 6ES7 322-1BL00-0AA0 | 6.6 | 21 | 138.6
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/6A | 6EP1233-1AA00 | 150 | 2 | 300
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/12A | 6EP1234-1AA00 | 300 | 4 | 1200
REDUNDANCY DIODE MODULE, 24VDC/10A | ULPEDDIO-10A | 8 | 1 | 8
REDUNDANCY DIODE MODULE, 24VDC/20A | ULPEDDIO-20A | 10 | 2 | 20
COOLING FAN WITH FILTER ASSEMBLY, 230VAC, RAL7035 | SK3323.107 | 19 | 4 | 76
PANEL TUBE LIGHT, 230VAC/11W | FMS200/111 | 11 | 4 | 44
LED INDICATION LAMP, 230VAC, RED (FOR 230VAC SUPPLY ON INDICATION) | 3SB14 01-2WZ3 | 1.5 | 3 | 4.5
LED INDICATION LAMP, 24VDC, GREEN (FOR 24VDC POWER SUPPLY ON INDICATION) | 3SB14 02-2HZ | 1.5 | 6 | 9
20% EXTRA | --- | 379.54 | 1 | 379.54
TOTAL (Watt) |  |  |  | 2277.24
Flow Rates are often given as ‘cubic feet per minute’ (cfm), so to convert to cubic meters per minute (m3/min) use the following multiplier:
m3/min = cfm x 0.0283
Air Flow for Rittal (SK3323.107) Fan (m3/hr) | 105
Total Fan used in panel are: | 4
So Air flow in Cubical is = (Air flow x fan qty) x 0.0283 | 118.86
= m3/min | 118.86
FORMULA
TEMP RISE IN PANEL | TOTAL POWER DISSIPATED (W) x 0.053
AIR FLOW IN CUBICAL(m3/min)
TEMP RISE IN PANEL | 1.0154
TOTAL TEMP RISE | = AMBIENT MAX.TEMP + TEMP RISE IN PANEL
| 31.0154 | Deg C

## CABINET-8
FOR MARSHALING CABINET-8
Description | TYPE | Power Diss(W). per module | QTY | Total Power Dissipated(W)
IM153-2, INTERFACE MODULE | 6ES7 153-2BA02-0XB0 | 5.5 | 6 | 33
CP341 WITH RS422 / RS485 INTERFACE | 6ES7 341-1CH02-0AE0 | 2.4 | 2 | 4.8
RS485 REPEATER FOR PROFIBUS | 6ES7 972-0AB01-0XA0 | 7.2 | 2 | 14.4
SM 331, 8 CHANNEL ANALOG I/P CARD, 4-20mA | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD T/C, 4-20mA | 6ES7 331-7KF02-0AB0 | 1 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, RTD | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG O/P CARD, 4-20mA | 6ES7 332-5HF00-0AB0 | 6 | 0 | 0
SM 321, 32 CHANNEL DIGITAL I/P CARD | 6ES7 321-1BL00-0AA0 | 6.5 | 12 | 78
SM 321, 16 CHANNEL SOE DIGITAL I/P CARD, 24VDC | 6ES7 321-7BH01-0AB0 | 4 | 0 | 0
SM 322, 32 CHANNEL DIGITAL O/P CARD | 6ES7 322-1BL00-0AA0 | 6.6 | 13 | 85.8
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/6A | 6EP1233-1AA00 | 150 | 2 | 300
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/12A | 6EP1234-1AA00 | 300 | 6 | 1800
REDUNDANCY DIODE MODULE, 24VDC/10A | ULPEDDIO-10A | 8 | 1 | 8
REDUNDANCY DIODE MODULE, 24VDC/20A | ULPEDDIO-20A | 10 | 3 | 30
COOLING FAN WITH FILTER ASSEMBLY, 230VAC, RAL7035 | SK3323.107 | 19 | 3 | 57
PANEL TUBE LIGHT, 230VAC/11W | FMS200/111 | 11 | 6 | 66
LED INDICATION LAMP, 230VAC, RED (FOR 230VAC SUPPLY ON INDICATION) | 3SB14 01-2WZ3 | 1.5 | 3 | 4.5
LED INDICATION LAMP, 24VDC, GREEN (FOR 24VDC POWER SUPPLY ON INDICATION) | 3SB14 02-2HZ | 1.5 | 8 | 12
20% EXTRA | --- | 498.7 | 1 | 498.7
TOTAL (Watt) |  |  |  | 2992.2
Flow Rates are often given as ‘cubic feet per minute’ (cfm), so to convert to cubic meters per minute (m3/min) use the following multiplier:
m3/min = cfm x 0.0283
Air Flow for Rittal (SK3323.107) Fan (m3/hr) | 105
Total Fan used in panel are: | 3
So Air flow in Cubical is = (Air flow x fan qty) x 0.0283 | 89.145
= m3/min | 89.145
FORMULA
TEMP RISE IN PANEL | TOTAL POWER DISSIPATED (W) x 0.053
AIR FLOW IN CUBICAL(m3/min)
TEMP RISE IN PANEL | 1.779
TOTAL TEMP RISE | = AMBIENT MAX.TEMP + TEMP RISE IN PANEL
| 31.779 | Deg C

## CABINET-9
FOR MARSHALING CABINET-9
Description | TYPE | Power Diss(W). per module | QTY | Total Power Dissipated(W)
IM153-2, INTERFACE MODULE | 6ES7 153-2BA02-0XB0 | 5.5 | 6 | 33
CP341 WITH RS422 / RS485 INTERFACE | 6ES7 341-1CH02-0AE0 | 2.4 | 0 | 0
RS485 REPEATER FOR PROFIBUS | 6ES7 972-0AB01-0XA0 | 7.2 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, 4-20mA | 6ES7 331-1KF01-0AB0 | 0.4 | 7 | 2.8
SM 331, 8 CHANNEL ANALOG I/P CARD T/C, 4-20mA | 6ES7 331-7KF02-0AB0 | 1 | 0 | 0
SM 331, 8 CHANNEL ANALOG I/P CARD, RTD | 6ES7 331-1KF01-0AB0 | 0.4 | 0 | 0
SM 331, 8 CHANNEL ANALOG O/P CARD, 4-20mA | 6ES7 332-5HF00-0AB0 | 6 | 2 | 12
SM 321, 32 CHANNEL DIGITAL I/P CARD | 6ES7 321-1BL00-0AA0 | 6.5 | 7 | 45.5
SM 321, 16 CHANNEL SOE DIGITAL I/P CARD, 24VDC | 6ES7 321-7BH01-0AB0 | 4 | 0 | 0
SM 322, 32 CHANNEL DIGITAL O/P CARD | 6ES7 322-1BL00-0AA0 | 6.6 | 10 | 66
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/6A | 6EP1233-1AA00 | 150 | 2 | 300
POWER SUPPLY, INPUT:230VAC, OUTPUT:24VDC/12A | 6EP1234-1AA00 | 300 | 6 | 1800
REDUNDANCY DIODE MODULE, 24VDC/10A | ULPEDDIO-10A | 8 | 1 | 8
REDUNDANCY DIODE MODULE, 24VDC/20A | ULPEDDIO-20A | 10 | 3 | 30
COOLING FAN WITH FILTER ASSEMBLY, 230VAC, RAL7035 | SK3323.107 | 19 | 3 | 57
PANEL TUBE LIGHT, 230VAC/11W | FMS200/111 | 11 | 6 | 66
LED INDICATION LAMP, 230VAC, RED (FOR 230VAC SUPPLY ON INDICATION) | 3SB14 01-2WZ3 | 1.5 | 3 | 4.5
LED INDICATION LAMP, 24VDC, GREEN (FOR 24VDC POWER SUPPLY ON INDICATION) | 3SB14 02-2HZ | 1.5 | 8 | 12
20% EXTRA | --- | 487.36 | 1 | 487.36
TOTAL (Watt) |  |  |  | 2924.16
Flow Rates are often given as ‘cubic feet per minute’ (cfm), so to convert to cubic meters per minute (m3/min) use the following multiplier:
m3/min = cfm x 0.0283
Air Flow for Rittal (SK3323.107) Fan (m3/hr) | 105
Total Fan used in panel are: | 3
So Air flow in Cubical is = (Air flow x fan qty) x 0.0283 | 89.145
= m3/min | 89.145
FORMULA
TEMP RISE IN PANEL | TOTAL POWER DISSIPATED (W) x 0.053
AIR FLOW IN CUBICAL(m3/min)
TEMP RISE IN PANEL | 1.7385
TOTAL TEMP RISE | = AMBIENT MAX.TEMP + TEMP RISE IN PANEL
| 31.7385 | Deg C