## Min IR Value
Jignesh.Parmar, www.electricalnotes.wordpress.com jiguparmar@yahoo.com
Minimum IR Value for Rotating Machine (AC or DC)
| Machine Terminal to Terminal Voltage |  | 0.44 | KVA
| IR (Min) for Machine |  | 1.44 | MΩ
Minimum IR Value for Transformer
[6 empty] | 50 Hz | 25 Hz | 2
| Frequency |  | 50 | Hz | 1 | 1.5 | 1
| Voltage Rating of winding under Test |  | 440 | Volt | 2 | 30 | 20
| Rated Capacity of Winding under Test |  | 1.6 | KVA | 3 | 30 | 20
Select Type of Transformer
| Tank Oil Filled T.C |  | 1 |  |  | 1.5
Without Tank Oil filled T.C
Dry or Compound Fill T.C
| IR (Min) for Transformer |  | 521.7758 | MΩ
Minimum IR Value for Cable
| Type of Cable |  |  | 1
| Type of Insulation Material |  |  | 3 |  | 1 | Paper | 2640 | 1 Core
[6 empty] | 2 | Varnished | 2460 | Multicore
| Outer Diameter of Conductor Insulation |  |  |  |  | 3 | ThermoPlastic-Polyethylene | 50000
| Diameter of Conductor |  |  |  |  | 4 | Composite-Polyethylene | 30000
|  |  |  | 0 |  | 5 | Polyvinyle Chloride (60°C) | 500
[6 empty] | 6 | Polyvinyle Chloride (75°C) | 2000
| IR (Min) for Cable |  |  | MΩ
[7 empty] | 50000 | 0
Minimum IR Value for Domestic Wiring
Case-1 | No of Outlet (All Point,Plugs with Fitting(Lamp etc)) |  | 25
| IR(min) value | Excellent | 2 | MΩ
Case-2 | No of Outlet (All Point,Plugs without Fitting(Lamp etc)) |  | 25
| IR(min) value | Excellent | 2 | MΩ
MINIMUM Insulation Resistance Value

## IR Value Graph
Jignesh.Parmar, www.electricalnotes.wordpress.com, jiguparmar@yahoo.com
Name of Equipment
Rated Voltage of Equipment |  | 230 |  |  | Volt
Recommended Megger Size |  | 100V DC or 250V DC | [6 empty] | 100 | 100V DC or 250V DC
Reference Temperature (°C) |  | 40 | [6 empty] | 200 | 100V DC or 250V DC
[9 empty] | 300 | 100V DC or 250V DC
Date | Measured IR Value (MΩ) | Temperature (°C) | Temperature Correction Factor | IR Value after Temperature Adjucment (MΩ) |  |  |  |  | 400 | 500V DC or 1000V DC
2010-01-01 | 3 | 42 | 1.1487 | 3.4461 |  | 3.4461 | 2010-01-01 |  | 500 | 500V DC or 1000V DC
2010-02-01 | 2 | 56 | 3.0314 | 6.0629 |  | 6.0629 | 2010-02-01 |  | 600 | 500V DC or 1000V DC
2010-03-01 | 4 | 55 | 2.8284 | 11.3137 |  | 11.3137 | 2010-03-01 |  | 700 | 500V DC or 1000V DC
2010-04-01 | 5 | 30 | 0.5 | 2.5 |  | 2.5 | 2010-04-01 |  | 800 | 500V DC or 1000V DC
2010-05-01 | 5 | 32 | 0.57435 | 2.8717 |  | 2.8717 | 2010-05-01 |  | 900 | 500V DC or 1000V DC
2010-05-02 | 2 | 34 | 0.65975 | 1.3195 |  | 1.3195 | 2010-05-02 |  | 1000 | 500V DC or 1000V DC
2010-05-03 | 2 | 34 | 0.65975 | 1.3195 |  | 1.3195 | 2010-05-03 |  | 1100 | 500V DC or 1000V DC
2010-05-05 | 5 | 10 | 0.125 | 0.625 |  | 0.625 | 2010-05-05 |  | 1200 | 500V DC or 1000V DC
2010-05-06 |  |  | 0 | 0 |  |  | 2010-05-06 |  | 1300 | 500V DC or 1000V DC
2010-05-07 |  |  | 0 | 0 |  |  | 2010-05-07 |  | 1400 | 500V DC or 1000V DC
2010-05-08 |  |  | 0 | 0 |  |  | 2010-05-08 |  | 1500 | 500V DC or 1000V DC
2010-05-09 |  |  | 0 | 0 |  |  | 2010-05-09 |  | 1600 | 500V DC or 1000V DC
2010-05-10 |  |  | 0 | 0 |  |  | 2010-05-10 |  | 1700 | 500V DC or 1000V DC
2010-05-11 |  |  | 0 | 0 |  |  | 2010-05-11 |  | 1800 | 500V DC or 1000V DC
2010-05-12 |  |  | 0 | 0 |  |  | 2010-05-12 |  | 1900 | 500V DC or 1000V DC
2010-05-13 |  |  | 0 | 0 |  |  | 2010-05-13 |  | 2000 | 500V DC or 1000V DC
|  |  | 0 | 0 |  |  |  |  | 2100 | 500V DC or 1000V DC
|  |  | 0 | 0 |  |  |  |  | 2200 | 500V DC or 1000V DC
|  |  | 0 | 0 |  |  |  |  | 2300 | 500V DC or 1000V DC
|  |  | 0 | 0 |  |  |  |  | 2400 | 500V DC or 1000V DC
|  |  | 0 | 0 |  |  |  |  | 2500 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 2600 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 2700 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 2800 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 2900 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 3000 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 3100 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 3200 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 3300 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 3400 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 3500 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 3600 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 3700 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 3800 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 3900 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 4000 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  |  | 4100 | 1000V DC or 2500V DC
2010-01-02 | 2 | 24 | 0.32988 | 0.65975 |  | 0.65975 | 2010-01-02 |  | 4200 | 1000V DC or 2500V DC
2010-01-01 | 2 | 30 | 0.5 | 1 |  | 1 | 2010-01-01 |  | 4300 | 1000V DC or 2500V DC
[9 empty] | 4400 | 1000V DC or 2500V DC
[9 empty] | 4500 | 1000V DC or 2500V DC
[9 empty] | 4600 | 1000V DC or 2500V DC
[9 empty] | 4700 | 1000V DC or 2500V DC
[9 empty] | 4800 | 1000V DC or 2500V DC
[9 empty] | 4900 | 1000V DC or 2500V DC
[9 empty] | 5000 | 2500V DC or 5000V DC
[9 empty] | 5100 | 2500V DC or 5000V DC
[9 empty] | 6000 | 2500V DC or 5000V DC
[9 empty] | 7000 | 2500V DC or 5000V DC
[9 empty] | 8000 | 2500V DC or 5000V DC
[9 empty] | 9000 | 2500V DC or 5000V DC
[9 empty] | 10000 | 2500V DC or 5000V DC
[9 empty] | 11000 | 2500V DC or 5000V DC
[9 empty] | 12000 | 2500V DC or 5000V DC
[9 empty] | 13000 | 50000V DC or 10000V DC
Insulation Resistance Value measurement

## Polarization Index
Jignesh.Parmar, www.electricalnotes.wordpress.com jiguparmar@yahoo.com
| Name of Equipment |  | adwa
| Rated Voltage of Equipment |  | 440 |  |  | Volt
| Recommended Megger |  | 500V DC or 1000V DC
Insulation Class
| Reference Temperature (°C) |  | 40
Date | Measured IR Value (MΩ) (for 10 Minitue) | Measured IR Value (MΩ) (for 1 Minitue) | Temperature (°C) | Temperature Correction Factor | Polarization Index Number after Temperature Adjucment | Insulation Condition |  | 1
2010-01-01 | 2 | 1 | 42 | 1.1487 | 2 | Questionable | 2 | 2010-01-01
2010-02-01 | 4 | 2 | 56 | 3.0314 | 2 | Questionable | 2 | 2010-02-01 | 100 | 100V DC or 250V DC
2010-03-01 | 5 | 1 | 55 | 2.8284 | 5 | Excellent | 5 | 2010-03-01 | 200 | 100V DC or 250V DC
2010-04-01 | 3 | 1 | 30 | 0.5 | 3 | OK | 3 | 2010-04-01 | 300 | 100V DC or 250V DC
2010-05-01 | 2 | 1 | 32 | 0.57435 | 2 | Questionable | 2 | 2010-05-01 | 400 | 500V DC or 1000V DC
2010-05-02 | 4 | 1 | 34 | 0.65975 | 4 | OK | 4 | 2010-05-02 | 500 | 500V DC or 1000V DC
2010-05-03 | 2 | 2 | 34 | 0.65975 | 1 | Poor | 1 | 2010-05-03 | 600 | 500V DC or 1000V DC
2011-06-05 | 3 | 4 | 42 | 1.1487 | 0.75 | Poor | 0.75 | 2011-06-05 | 700 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 800 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 900 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 1000 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 1100 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 1200 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 1300 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 1400 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 1500 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 1600 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 1700 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 1800 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 1900 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 2000 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 2100 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 2200 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 2300 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 2400 | 500V DC or 1000V DC
|  |  |  | 0 | 0 |  |  |  | 2500 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 2600 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 2700 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 2800 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 2900 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 3000 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 3100 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 3200 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 3300 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 3400 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 3500 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 3600 | 1000V DC or 2500V DC
|  |  |  | 0 | 0 |  |  |  | 3700 | 1000V DC or 2500V DC
2010-01-01 | 2 | 3 | 23 | 0.30779 | 0.66667 | Poor | 0.66667 | 2010-01-01 | 3800 | 1000V DC or 2500V DC
[9 empty] | 3900 | 1000V DC or 2500V DC
[9 empty] | 4000 | 1000V DC or 2500V DC
[9 empty] | 4100 | 1000V DC or 2500V DC
[9 empty] | 4200 | 1000V DC or 2500V DC
[9 empty] | 4300 | 1000V DC or 2500V DC
[9 empty] | 4400 | 1000V DC or 2500V DC
[9 empty] | 4500 | 1000V DC or 2500V DC
[9 empty] | 4600 | 1000V DC or 2500V DC
[9 empty] | 4700 | 1000V DC or 2500V DC
[9 empty] | 4800 | 1000V DC or 2500V DC
[9 empty] | 4900 | 1000V DC or 2500V DC
[9 empty] | 5000 | 2500V DC or 5000V DC
[9 empty] | 5100 | 2500V DC or 5000V DC
[9 empty] | 6000 | 2500V DC or 5000V DC
[9 empty] | 7000 | 2500V DC or 5000V DC
[9 empty] | 8000 | 2500V DC or 5000V DC
[9 empty] | 9000 | 2500V DC or 5000V DC
[9 empty] | 10000 | 2500V DC or 5000V DC
[9 empty] | 11000 | 2500V DC or 5000V DC
[9 empty] | 12000 | 2500V DC or 5000V DC
[9 empty] | 13000 | 50000V DC or 10000V DC
POLARIZATION INDEX Value measurement
Class A
Class B
Class C
Class F
Class H

## Earth Resistivity
[6 empty] | Jignesh.Parmar, www.electricalnotes.wordpress.com, jiguparmar@yahoo.com | [5 empty] | The Earth Resistance Value
[13 empty] | Power Station | < 0.5Ω
[9 empty] | Earth Tester/Megger (4 Terminals) |  |  |  | EHT SubStation | < 1.0Ω
[13 empty] | 66KV SuStation | < 2.0Ω
[9 empty] | P1 | P2 |  |  | D.P Structure | <5.0Ω
Direction-I | Date | Electrode Spacing (S) (Meter) | Megger Rading in Ohms | Earth Resistivity Ohm-Meter | Remarks | [7 empty] | Tower Foot Resistance | <10.0Ω
1 | 2010-01-01 | 1 |  | 0 |  |  |  |  | C1 | C2
2 |  | 2 |  | 0
3 |  | 5 |  | 0
4 |  | 10 |  | 0
5 |  | 15 |  | 0
6 |  | 25 |  | 0
7 |  | 50 |  | 0 | [8 empty] | 30 to 50 Cm
Direction-II | Date | Electrode Spacing (S) (Meter) | Megger Rading in Ohms | Earth Resistivity Ohm/Meter | Remarks
1 |  | 1 |  | 0
2 |  | 2 |  | 0 |  |  | S |  | S |  | S
3 |  | 5 |  | 0
4 |  | 10 |  | 0
5 |  | 15 |  | 0
6 |  | 25 |  | 0 |  |  | Location of Earth Resistivity Measurement
7 |  | 50 |  | 0
1
Direction-III | Date | Electrode Spacing (S) (Meter) | Megger Rading in Ohms | Earth Resistivity Ohm/Meter | Remarks
1 |  | 1 |  | 0 |  |  | 4 |  | 5 |  | 6 |  | 2
2 |  | 2 |  | 0
3 |  | 5 |  | 0
4 |  | 10 |  | 0
5 |  | 15 |  | 0
6 |  | 25 |  | 0 | [5 empty] | 3
7 |  | 50 |  | 0
Direction-IV | Date | Electrode Spacing (S) (Meter) | Megger Rading in Ohms | Earth Resistivity Ohm/Meter | Remarks
1 |  | 1 |  | 0
2 |  | 2 |  | 0 |  |  |  |  | Earth Tester/Megger (3 Terminals)
3 |  | 5 |  | 0 | [5 empty] | P
4 |  | 10 |  | 0
5 |  | 15 |  | 0 |  |  |  |  | E | C
6 |  | 25 |  | 0
7 |  | 50 |  | 0
Direction-V | Date | Electrode Spacing (S) (Meter) | Megger Rading in Ohms | Earth Resistivity Ohm/Meter | Remarks
1 |  | 1 |  | 0
2 |  | 2 |  | 0
3 |  | 5 |  | 0
4 |  | 10 |  | 0 |  |  |  | 75 Feet |  |  | 75 Feet
5 |  | 15 |  | 0
6 |  | 25 |  | 0
7 |  | 50 |  | 0
Direction-VI | Date | Electrode Spacing (S) (Meter) | Megger Rading in Ohms | Earth Resistivity Ohm/Meter | Remarks
1 |  | 1 |  | 0
2 |  | 2 |  | 0
3 |  | 5 |  | 0
4 |  | 10 |  | 0
5 |  | 15 |  | 0
6 |  | 25 |  | 0
7 |  | 50 |  | 0
Earth Resistivity Value Measurement