## PF calculator
Power Factor Table Calculator
SELECTING CAPACITOR SIZE |  |  |  | Automatic Capacitor Bank Sizing
The following graphic tool can be used to estimate the capacitor kVAR required to improve PF of a single load or entire power system. Actual power factor, peak kilowatt demand and desired PF are required. The best source for this information is the monthly utility bill or other local monitoring equipment. A calculation of each months data for a 12 month period is recommended to determine the maximum kVAR, and optimal stages required. |  |  |  |  | Example: How much kVAR is required to correct an entire
480V system to a 90% power factor when the peak kilowatt
demand month was 620kW at a 65% power factor?
Use the formula: kVAR = kW x kW FACTOR
From the kW FACTOR calculator below , the FACTOR
is 0.685
Therefore: kVAR = 620 x .685 = 425kVAR
|  | Existing P.F (%) |  |  |  | 70
|  | Desired P.F. (%) |  |  |  | 94
|  | Load (kW) |  |  |  | 1000
|  |  | Kilowatt Factor |  | 0.65725
|  |  | Required kVAR |  | 657.2525
Note: the outcome of this calculator is for estimation purpose only. Please use the quotation form to request a formal quotation from Schneider Electric. Contact Schneider Electric Power Quality Correction Group at 905-678-6699 if you have questions.