## Sheet1
Jignesh.Parmar www.electricalnotes.wordpress.com
| :Transformer Detail: |  |  | :Transformer Detail:
| Transformer Size | 1000 | KVA | Transformer Size |  | 1000 | KVA
| Transformer Secondary Voltage:(v2) | 480 | Volt | Transformer Secondary Voltage:(v2) |  | 480 | Volt
| % Impedance: (z) | 5.75% |  | % Impedance: (z) |  | 5.75%
| Allowable Voltage Drop in System: | 10% |  | Allowable Voltage Drop in System: |  | 10%
| :Motor Detail ( Only One No of Motor): |  |  | :Motors Detail ( More Than One No of Motor):
| Motor Size: | 300 | Kw | Total KW of Three Phase Motors: |  | 300 | Kw
| Volt (vm): (L-L) | 460 | Volt | Total KW of Single Phase Motors: |  | 5 | Kw
| Power Factor: | 0.8 |  | Volt: (L-L) |  | 460 | Volt
| Motor KVA | 240 | KVA | Volt: (L-N) |  | 265.5889 | Volt
| Motor Code: (Kva/Hp) |  |  | Power Factor: |  | 0.8
| InRush Current at Starting:(Enter If you know otherwise leave it blank) |  |  | Locaked Rotor Current: (Max) |  | 450%
| Enter Motor Full Load Current(Enter If you know otherwise leave it blank ) |  |  | Total Three Phase Motors Full Load Current |  | 470.6798 | Amp
| Motor Full Load Current: (ILM) | 470.6798 | Amp | Total Single Phase Motors Full Load Current |  | 23.5326 | Amp
| Locaked Rotor Current Multiplier: (Min) | 4.1 |  | Total Motors Full Load Current |  | 494.2124 | Amp
| Locaked Rotor Current Multiplier: (Max) | 4.5 |  | Motor InRush KVA At Starting |  | 1771.87 | KVA
| Locaked Rotor Current (L1): (Min) | 1929.7871 | Amp
| Locaked Rotor Current (L2): (Max) | 2118.059 | Amp
| Motor InRush KVA At Starting: (IrsM) | 1687.5 | KVA
| How many times Motor Starts per Hours | 2
| :Calculations: |  |  | :Calculations:
| Full Load Current of Transformer : (ILX) | 1202.8483 | Amp | Full Load Current of Transformer : (IL) |  | 1202.8483 | Amp
| Short Circuit Current at Transformer Secondary: (Isc) | 20919.1017 | Amp | Short Circuit Current at Transformer Secondary: (Isc) |  | 20919.1017 | Amp
| Max KVA of Transformer at Isc: Q1 | 17391.3043 | KVA | Max KVA of Transformer at Isc |  | 17391.3043 | KVA
| Motor InRush KVA At Starting:(IrsM) | 1687.5 | KVA | Motor InRush KVA At Starting |  | 1771.87 | KVA
| Voltage Drop at Transformer Secondary Due to Motor inRush: (Vd) | 9.703% | 90.3% | Voltage Drop at Transformer Secondary Due to Motor inRush |  | 10.19% | 89.81%
| Transformer Secondary Voltage | 433.425 | Volt | Transformer Secondary Voltage |  | 431.0964 | Volt
| :Result: |  |  | :Result:
| (1) Motor Full Load Current <= 65% Transformer Full Load Current | Yes |  | (1) Motor Full Load Current <= 65% Transformer Full Load Current |  | Yes
| (2) Voltage Drop at Transformer Secondary Due to Motor inRush | Low |  | (2) Voltage Drop at Transformer Secondary Due to Motor inRush |  | High
| (3) Transformer Size:(20% Added due to motor starts more than once/Hour) | 1200 | Kva | (3) Transformer Size: |  | 1000 | KVA
| Size of Transformer is Adequate |  |  | Increase Size of Transformer
Calculation Formulas:
ILX=KVA/(1.732xv2)
ILM=(Kwx1000)/(1.732xVmxP.F)
Isc=ILx/z
Q1=(v2xISCxILMx1.732)/1000
IrsM=(VmxL2x1.732)/1000
Vd=IrsM/Q1
Code Letter (KVA per HP) -Locked Rotor Current
| Motor Code | Min | Max
1 | A | 3.15
2 | B | 3.16 | 3.55
3 | C | 3.56 | 4
4 | D | 4.1 | 4.5
5 | E | 4.6 | 5
6 | F | 5.1 | 5.6
7 | G | 5.7 | 6.3
8 | H | 6.4 | 7.1
9 | J | 7.2 | 8
10 | K | 8.1 | 9
11 | L | 9.1 | 10
12 | M | 10.1 | 11.2
13 | N | 11.3 | 12.5
14 | P | 12.6 | 14
15 | R | 14.1 | 16
16 | S | 16.1 | 18
17 | T | 18.1 | 20
18 | U | 20.1 | 22.4
19 | V | 22.5
4
4.1
4.5
Note on E24: If motor is to be started more than once per hour add 20% additional KVA
Calculate Size of Transformer and Voltage drop due to Starting of Large size Motor